## Tabelle1
Ni1000 according to DIN 43760 connected to a PCD2.W220
By adapting the parameters the same table can be used for all analogue modules with a constant reference voltage and a fixed resistance in series to the resistance to be measured
Reference Voltage |  | Fixed resistance |  | (7.5kOhm for W220 and W340)
10 | Volt | 7500 | Ohm
Range of the A/D converter, 0 to (2.5V for W340) |  | Resolution of the A/D converter, respectively 4095 when using the FBoxes of the HEAVAC Library
2.5 | Volt | 1023 | Counts
Temp °C | DIN 43760 | Digital Value | Estimated resolution °C/Count
Ohm
15 | 1083.7727 | 517
20 | 1112.3645 | 529 | 0.41667
25 | 1141.2922 | 540 | 0.45455
30 | 1170.5577 | 552 | 0.41667
35 | 1200.1633 | 564 | 0.41667
40 | 1230.1117 | 577 | 0.38462
45 | 1260.4061 | 589 | 0.41667
50 | 1291.05 | 601 | 0.41667
55 | 1322.0474 | 613 | 0.41667
60 | 1353.4026 | 626 | 0.38462
65 | 1385.1205 | 638 | 0.41667
70 | 1417.2061 | 650 | 0.41667
75 | 1449.6652 | 663 | 0.38462
80 | 1482.5037 | 675 | 0.41667
85 | 1515.7279 | 688 | 0.38462
90 | 1549.3447 | 701 | 0.38462
95 | 1583.3612 | 713 | 0.41667
100 | 1617.785 | 726 | 0.38462
105 | 1652.6239 | 739 | 0.38462
110 | 1687.8864 | 752 | 0.38462
Values for the 20 point conversion FBox
51.7 | 15
52.9 | 20
54 | 25
55.2 | 30
56.4 | 35
57.7 | 40
58.9 | 45
60.1 | 50
61.3 | 55
62.6 | 60
63.8 | 65
65 | 70
66.3 | 75
67.5 | 80
68.8 | 85
70.1 | 90
71.3 | 95
72.6 | 100
73.9 | 105
75.2 | 110